## Sheet1
Battery Sizing calculation |  | Falcon 7KM | Falcon X5
UPS Rating (KVA) | = | 100 | 30
Actual Load on UPS (KVA) | = | 100 | 30
Power in KW (VA * Pf) |  | 80 | 24
Inverter Efficiency (n) | = | 96% | 95%
No of Battery | = | 38 | 32
Number of battery banks / strings | = | 1 | 1
End Cell Voltage (ECV) | = | 1.75 | 1.75
Back up time required (in mins) |  | 15 | 30
Watts/Battery Required |  | 2192.9825 | 789.4737
Watts/Battery Required /String |  | 2192.9825 | 789.4737
Nearest battery AH Selected referring to the manuacturer chart at C20 |  | 120 | 65
Watts/Battery provided by the selected battery |  | 2255 | 798
Nominal voltage of each batteries | = | 12 | 12
Number of batteries per UPS | = | 38 | 32
Number of battery banks / strings | = | 1 | 1
Total number of batteries per UPS |  | 38 | 32
Total VAH |  | 54720 | 24960